## Input
Upper Section | [6 empty] | Temperature Profile
initial Temperature C | 5 | Internals |  | Hot Spot |  |  | Exterior Temperature | 5
Max heat in (W) | 64000 | area (m^2) | 300 | area (m^2) | 30 |  | Target Temperature | 17
volume (m^3) | 1000 | internal material type | Brick | internal material type | Brick |  | Target Level | Lower | # not used for now
densityC | 1206 | internal material thickness (cm) | 17.5 | internal material thickness (cm) | 17.5
conductive heat to lower level | 20 | Radiant Heat in (W) | 0 | external material type | Brick
airchanges per hour | 0.5 |  |  | external material thickness (cm) | 0
area to lower level (m^3) | 500 |  |  | airbythotspot | 60
ROOF |  | WALL |  | WINDOWS |  |  | ROUND THICKNESSES TO NEAREST 0.5CM!!
area (m^2) | 750 | area (m^2) | 150 | area (m^2) | 30 | iloc[7-14] | DO NOT CHANGE LAYOUT
internal material type | Stramit board | internal material type | Brick | material | Glass |  | AREA MUST NOT BE ZERO AS CAUSES ERROR -> MAKE V SMALL
internal material thickness (cm) | 5 | internal material thickness (cm) | 17.5 | type | single |  | all initial tempterature should be the same otehrwise not good ovnergence
external material type | Slate | external material type | Brick | Radiant Heat in (W) | 0 |  | hotspot should be higher than room temp
external material thickness (cm) | 0 | external material thickness (cm) | 0 | thickness | 10 |  | laso t exterior should be this initial temperaute
Radiant Heat in (W) | 0 | Radiant Heat in (W) | 8000 |  |  |  | NO BIG TEMPERATURE DIFFERNCES AT T=0!
Middle Section
initial Temperature C | 5 | Internals |  | Hot Spot
Max heat in (W) | 0 | area (m^2) | 0.01 | area (m^2) | 0.01
volume (m^3) | 1000 | internal material type | Brick | internal material type | Stramit board
densityC | 1206 | internal material thickness (cm) | 17.5 | internal material thickness (cm) | 5
conductive heat to lower level | 20 | Radiant Heat in (W) | 0 | external material type | Brick
airchanges per hour | 0.5 |  |  | external material thickness (cm) | 0
area to lower level (m^3) | 500 |  |  | airbythotspot | 60.3
ROOF |  | WALL |  | WINDOWS
area (m^2) | 0.001 | area (m^2) | 150 | area (m^2) | 30
internal material type | Slate | internal material type | Brick | material | Glass
internal material thickness (cm) | 15 | internal material thickness (cm) | 17.5 | type | single
external material type | Slate | external material type | Brick | Radiant Heat in (W) | 0
external material thickness (cm) | 0 | external material thickness (cm) | 0 | thickness | 1
Radiant Heat in (W) | 0 | Radiant Heat in (W) | 8000
Lower Section
initial Temperature C | 5 | Internals |  | Hot Spot |  | Underfloor Heating
Max heat in (W) | 0 | area (m^2) | 0.01 | area (m^2) | 0.01 | area (m^2) | 0.01
volume (m^3) | 1000 | internal material type | Brick | internal material type | Brick | internal material type | Brick
densityC | 1206 | internal material thickness (cm) | 17.5 | internal material thickness (cm) | 17.5 | internal material thickness (cm) | 17.5
conductive heat to lower level | 0 | Radiant Heat in (W) | 0 | external material type | Brick | external material type | Polystyrene or similar
airchanges per hour | 0.5 |  |  | external material thickness (cm) | 0 | external material thickness (cm) | 10
area to lower level (m^3) | 500 |  |  | airbythotspot | 50 | Radiant Heat in (W) | 50
ROOF |  | WALL |  | FLOOR |  | WINDOWS
area (m^2) | 0.001 | area (m^2) | 150 | area (m^2) | 500 | area (m^2) | 30
internal material type | Slate | internal material type | Brick | internal material type | Carpet (5mm thick) | material | Glass
internal material thickness (cm) | 15 | internal material thickness (cm) | 17.5 | internal material thickness (cm) | 0.5 | type | single
external material type | Slate | external material type | Brick | external material type | Stone | Radiant Heat in (W) | 0
external material thickness (cm) | 0 | external material thickness (cm) | 0 | external material thickness (cm) | 50 | thicnkess | 1
Radiant Heat in (W) | 0 | Radiant Heat in (W) | 8000 | Radiant Heat in (W) | 0

## Materials
Material |  | Thermal conductivity | Specific heat capacity | Density | DensityC | HTCconv
| Material number | W/m/oC | J/kg/oC | kg/m3 |  | ? | note
Stone | 1 | 1.7 | 710 | 2500 | 1775000 | 6.4 | sandstone / 2.3 - 2.8
Brick | 2 | 1 | 840 | 2000 | 1680000 | 6.4 | dense / hard
Gypsom | 3 | 0.17 | 1090 | 2300 | 2507000 | 6.4
lime plaster | 4 | 0.8 | 864 | 1820 | 1572480 | 6.4 | http://www.tara.tcd.ie/bitstream/handle/2262/75851/RW%20SP%20Coinvedi%202015.pdf?sequence=1
Insulating plaster | 5 | 0.045 | 1000 | 360 | 360000 | 6.4 | https://www.ecologicalbuildingsystems.com/product/diathonite-evolution#technical-details
Wood (pine) | 6 | 0.15 | 1500 | 510 | 765000 | 6.4 | red / scots
Wood (oak) | 7 | 0.17 | 2400 | 740 | 1776000 | 6.4 | english brown
Carpet (5mm thick) | 8 | 0.05 | 1700 | 1200 | 2040000 | 6.4 | https://carpetlayerwhangarei.nz/carpet-advice.php
Polystyrene or similar | 9 | 0.035 | 1400 | 30 | 42000 | 6.4 | 1300-1500 / .015 - .03
Lead | 10 | 35 | 129 | 11350 | 1464150 | 6.4
Slate | 11 | 2.01 | 760 | 3000 | 2280000 | 6.4 | 2.6-3.3
Steel | 12 | 43 | 490 | 7820 | 3831800 | 6.4 | 1% carbon
Glass | 13 | 1.05 | 700 | 2500 | 1750000 | 6.4 | quartz glass / 2.4-2.8
Stramit board | 14 | 0.1 | 1300 | 380 | 494000 | 6.4
Glass mineral wool | 15 | 0.035 | 1030 | 20 | 20600 | 6.4 | https://www.greenspec.co.uk/building-design/insulation-materials-thermal-properties/
single
double

## Heat generator system model
Energy in to boiler (kW) | 50
Heat generator type | electric |  | condensing | 0.95
Boiler efficiency | 1 |  | non-condensing | 0.6
Design boiler output temperature (C) | 70 |  | electric | 1
|  |  | air to water heat pump | 3
Length of pipework (m) | 50 |  | ground source heat pump | 3.5
Pipework outside diameter (mm) | 75
Assumed thickness (mm) | 5
Radiator water volume (@0.008m3/kW) | 0.4 | m3
Radiator mass @47kg/kW | 2350 | kg
Specific heat capacity water | 4.182 | kJ/kgK
Density water | 998 | kg/m3
Specific heat capacity pipe (steel) | 0.49 | kJ/kgK
Density (steel) | 7820 | kg/m3
Water volume | 0.56592 | m3
Steel volume | 0.35942 | m3
water mass | 564.7835 | kg
Steel mass | 2810.636 | kg
Water thermal inertia | 2361.9247 | kJ/K
Steel thermal inertia | 1377.2117 | kJ/K
Total thermal inertia | 3739.1364 | kJ/K | Rate of temperature rise (no heat loss) | K/s | 0.013372
|  |  | time to reach | 70 | 1.4541 | hours
but heat loss as it warm up will increase this time!!!