## Geometry and fabric definition
Data input sheet for church heating calculation:
|  |  | test case values | Hidden from user:
Total building air changes per hour |  |  | 0.5
Upper section
Max convective heat in to upper section | W |  | 38000
Total radiant heat in to upper section | W |  | 0
Total volume | m3 |  | 1000
Roof / ceiling area | m2 |  | 500 | Air to surface heat transfer coefficient | W/m2C | 9
Roof construction:
internal material |  |  | 14
internal material thickness | mm |  | 50
external material
external material thickness | mm |  | 0
Proportion of radiant heat in to roof | % |  | 0
Wall area | m2 |  | 120 | Air to surface heat transfer coefficient | W/m2C | 3
Wall construction:
internal material |  |  | 1
internal material thickness | mm |  | 175
external material
external material thickness | mm
Proportion of radiant heat in to wall | % |  | 100
Window area | m2 |  | 30 | Air to surface heat transfer coefficient | W/m2C
Window construction:
stained glass |  |  |  | Heat transfer coefficient (U value) |  | 6
single glazing |  |  | 1 | Heat transfer coefficient (U value) |  | 5.6
double glazing |  |  |  | Heat transfer coefficient (U value) |  | 2.8
internal material
internal material thickness | mm
external material
external material thickness | mm
Proportion of radiant heat to window | % |  | 0
Internals surface area | m2 |  | 500 | Air to surface heat transfer coefficient | W/m2C | 6.4
Internals volume | m3 |  | 2.5
Internals material |  |  | 12
Middle section |  |  |  | upper to middle section heat transfer coefficient | W/m2C | 20
Max convective heat in to middle section | W |  | 0
Total radiant heat in to middle section | W |  | 22000
Total volume | m3 |  | 1000
Roof / ceiling area | m2 |  | 0 | Air to surface heat transfer coefficient | W/m2C
Roof construction:
internal material
internal material thickness | mm
external material
external material thickness | mm
Proportion of radiant heat in to roof | %
Wall area | m2 |  | 120 | Air to surface heat transfer coefficient | W/m2C | 3
Wall construction:
internal material |  |  | 1
internal material thickness | mm |  | 175
external material
external material thickness | mm
Proportion of radiant heat in to wall | % |  | 100
Window area | m2 |  | 30 | Air to surface heat transfer coefficient | W/m2C
Window construction:
stained glass |  |  |  | Heat transfer coefficient (U value) |  | 6
single glazing |  |  | 1 | Heat transfer coefficient (U value) |  | 5.6
double glazing |  |  |  | Heat transfer coefficient (U value) |  | 2.8
internal material
internal material thickness | mm
external material
external material thickness | mm
Proportion of radiant heat to window | % |  | 0
Internals surface area | m2 |  | 0 | Air to surface heat transfer coefficient | W/m2C
Internals volume | m3 |  | 0
Internals material
Lower section |  |  |  | middle to lower section heat transfer coefficient | W/m2C | 20
Max convective heat in to lower section | W |  | 0
Total radiant heat in to lower section | W |  | 22000
Heat in to floor (below middle material, to simulate underfloor heating) | W |  | 0
Total volume | m3 |  | 1000
Roof / ceiling area | m2 |  | 0 | Air to surface heat transfer coefficient | W/m2C
Roof construction:
internal material
internal material thickness | mm
external material
external material thickness | mm
Proportion of radiant heat in to roof | %
Wall area | m2 |  | 120 | Air to surface heat transfer coefficient | W/m2C | 3
Wall construction:
internal material |  |  | 1
internal material thickness | mm |  | 175
external material
external material thickness | mm
Proportion of radiant heat in to wall | % |  | 80
Window area | m2 |  | 30 | Air to surface heat transfer coefficient | W/m2C
Window construction:
stained glass |  |  |  | Heat transfer coefficient (U value) |  | 6
single glazing |  |  | 1 | Heat transfer coefficient (U value) |  | 5.6
double glazing |  |  |  | Heat transfer coefficient (U value) |  | 2.8
internal material
internal material thickness | mm
external material
external material thickness | mm
Proportion of radiant heat to window | % |  | 0
Floor area | m2 |  | 500 | Air to surface heat transfer coefficient | W/m2C | 3
Floor construction:
internal material |  |  | 8
internal material thickness | mm |  | 5
middle material |  |  | 2
middle material thickness | mm |  | 100
external material |  |  | 1
external material thickness | mm |  | 200
Proportion of radiant heat in to floor | % |  | 20
Internals surface area | m2 |  | 0 | Air to surface heat transfer coefficient | W/m2C
Internals volume | m3 |  | 0
Internals material |  |  | 0
|  | Material number |  | for properties, see 'materials data sheet (hidden)
Stone |  | 1
Brick |  | 2
Gypsom |  | 3
lime plaster |  | 4
Insulating plaster |  | 5
Wood (pine) |  | 6
Wood (oak) |  | 7
Carpet (5mm thick) |  | 8
Polystyrene or similar |  | 9
Lead |  | 10
Slate |  | 11
Steel |  | 12
Glass |  | 13
Stramit board |  | 14
User defined: |  | User
Thermal conductivity | W/m/oC
Specific heat capacity | J/kg/oC
Density | kg/m3

## Heat and outside temp profile
Outside temperature profile:
| 0:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monday
Tuesday
Wednesday
Thursday
Friday
Saturday
Heating profile UPPER SECTION (1 = on, 0 = off)
| 0:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
Sunday | [9 empty] | 1 | 1 | 1 | 1 | 1
Monday
Tuesday
Wednesday
Thursday
Friday
Saturday
Heating profile MIDDLE SECTION (1 = on, 0 = off)
Same as upper? | Yes
| 0:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
Sunday | [9 empty] | 1 | 1 | 1 | 1 | 1
Monday
Tuesday
Wednesday
Thursday
Friday
Saturday
Heating profile LOWER SECTION (1 = on, 0 = off)
Same as upper? | Yes
| 0:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
Sunday | [9 empty] | 1 | 1 | 1 | 1 | 1
Monday
Tuesday
Wednesday
Thursday
Friday
Saturday
Target internal temperature profile (assumed at Lower Section)
| 0:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
Sunday | [9 empty] | 17 | 17 | 17 | 17 | 17
Monday
Tuesday
Wednesday
Thursday
Friday
Saturday
Is there a simpler way to define this?

## materials data sheet (hidden)
|  | https://www.engineeringtoolbox.com/thermal-conductivity-d_429.html | https://www.engineeringtoolbox.com/specific-heat-capacity-d_391.html | https://www.engineeringtoolbox.com/density-solids-d_1265.html
|  | Thermal conductivity | Specific heat capacity | Density
| Material number | W/m/oC | J/kg/oC | kg/m3 | note
Stone | 1 | 1.7 | 710 | 2500 | sandstone / 2.3 - 2.8
Brick | 2 | 1 | 840 | 2000 | dense / hard
Gypsom | 3 | 0.17 | 1090 | 2300
lime plaster | 4 | 0.8 | 864 | 1820 | http://www.tara.tcd.ie/bitstream/handle/2262/75851/RW%20SP%20Coinvedi%202015.pdf?sequence=1
Insulating plaster | 5 | 0.045 | 1000 | 360 | https://www.ecologicalbuildingsystems.com/product/diathonite-evolution#technical-details
Wood (pine) | 6 | 0.15 | 1500 | 510 | red / scots
Wood (oak) | 7 | 0.17 | 2400 | 740 | english brown
Carpet (5mm thick) | 8 | 0.05 |  | 1200 | https://carpetlayerwhangarei.nz/carpet-advice.php | https://www.greenspec.co.uk/building-design/thermal-mass/
Polystyrene or similar | 9 | 0.035 | 1400 | 30 | 1300-1500 / .015 - .03
Lead | 10 | 35 | 129 | 11350
Slate | 11 | 2.01 | 760 | 3000 | 2.6-3.3
Steel | 12 | 43 | 490 | 7820 | 1% carbon
Glass | 13 | 1.05 | 700 | 2500 | quartz glass / 2.4-2.8
Stramit board | 14 | 0.1 | 1300 | 380